Project Nheengatu: EPICS support for CompactRIO FPGA and LabVIEW-RT
Dawood Alnajjar - SOL

---
LabVIEW
National instruments general interface to configure the CRIO through VI development. VIs
Can be implmented on the FPGA or LinuxRT (labviewRT).

---
CompactRIO 9045
Has a Xilinx Kintex 7 FPGA and an atom processor running LinuxRT
Pluggable modules

---
Objective
Input and output binary and analog data, fast trigger counting,
fine control using EPICS and CRIO
FPGA
LabviewRT (runs in LinuxRT)
Users

---
Nheengatu architecture
(2)
NiFpgaHelp.so
LibCrioLinux.so
CrioLinux.h
(3)
EPICs device
Support
CrioDevSup.a/so
(1)
Labview Project:
FPGA and
Labview realtime
variables
(4)
EPICS IOC
cfg.ini
substitutions
Parts in red : needs user intervention
(1) LabviewRT : Developed extensions to open a shared memory and write/read from/to it
     FPGA : Use C API generator to generate addresses associated with variables
(2) LibCrioLinux.so : abstraction layer to reads and writes to shared memory and
        FPGA addresses of the variables using a reference “name”
      NiFpgaHelp.so : Contains all NI specific functions
(3) Device support : EPICS library that contains 5 types of records : BI, BO, AI, AO, Scaler,
        Waveform, and contains functions to initialize CRIO from IOC
(4) EPICS IOC : IOC (no custom code, just db templates) that has access to all device
        support types

---
1.1 Handling FPGA variables (1/6)
BIs: Concatenate and connect to U64 Indicator
BOs: As is (boolean indicator)
Binary output : as is
Binary input : Convert to 64-bit U64

---
1.1 Handling FPGA variables (2/6)
AI and AO handling : Convert to fixed-point or single precision floating point
Fixed-point handling
Single precision floating point handling
Analog input : use cast to U64 polymorphic VI
Analog input : Convert to float
Analog output : Convert to FXP
Analog output : use cast to fixed-point polymorphic VI

---
1.1 FPGA variables (3/6)
Scaler
Scaler digital
Scaler IP in VHDL
Scaler Analog
Validated with testbench
If not all 64 counters are used, the logic can simply be optimized by reducing the size of the fixed input arrays.
FPGA utilization can be reduced by approximately 15% if this optimization is applied

---
1.1 Handling FPGA variables (4/6)
Reading arrays : instantiate indicator array
I08 I16, I32, I64
U08, U16, U32, U64
Single precision floating point

---
1.1 FPGA variables (5/6)
Generates header file with addresses
Generate bitstream and C API files
The address of each variable must be noted for the cfg.ini file
(or automation tools can be used).

---
1.1 FPGA variables (6/6)
Make sure that non of your indicators and controls are omitted by abiding with the data types defined above!

---
1.2 LabviewRT variables
Four Vis were developed to synchronize variable/array exchange with EPICS
IOC Shared memory initialize.vi
Initializes shared memory. All input can be left as default
IOC Shared memory de-initialize.vi
de-initializes shared memory.
SM read and increment.vi (polymorphic VI)
Reads the variable (from EPICS) when setting the polymorphic VI
SM write and increment.vi (polymorphic VI)
Writes the variable (to EPICS) when setting the polymorphic VI
All VI MUST be chained with <ptr in> and <ptr out>.
The index of the variable must be noted for the cfg.ini file.

---
2 & 3 libCrioLinux.so and EPICS device support
NO alteration or re-compile is required!
Device support library path needs to be indicated explicitely in the IOC

---
4.1 EPICS IOC (1/10)
As long as the associated DB files are used, the IOC does not need to be compiled either!

---
4.2 EPICS IOC – CFG.INI (2/10)
If changed, must be changed in labview RT VI too!
Disabling shared memory disables all labview RT variable processing.

---
4.2 EPICS IOC – CFG.INI (3/10)
- 2 types of variables: labview RT variables, and FPGA variables
- The library distinguishes the RT variables type and its size through its name

---
4.2 EPICS IOC – CFG.INI (4/10)
- [BIAddresses]
  - Address/index of BI
- [BI0]: index -name relation of each bit in the 64 bits (FPGA)
- [AO]: Address/index of each available output analog variable
- [AI]: Address/index of each available input analog variable
- [BO]: Address/index of each available output digital variable

---
4.2 EPICS IOC – CFG.INI (5/10)
- [WAVEFORM]
  - List pf waveforms (RT & FPGA)
- [WAVEFORMXX]:
  - details of WAVEFORMXX
- [FXP_XX]:
  - Details of FXP_XX

---
4.2 EPICS IOC – CFG.INI (6/10)

---
4.2 EPICS IOC – Settings (7/10)
Introduce path of deviceSupportCrio to IOC
$(TOP)/configure/RELEASE
Introduce deviceSupportCrio library name to IOC
$(TOP)/CRIOApp/src/Makefile

---
4.2 EPICS IOC – st.cmd (8/10)
Even the command file does not need any modifications!

---
4.2 EPICS IOC – templates (9/10)
AI db substitutions
This name must correspond to the name in the cfg.ini file
AI db template

---
4.2 Automatic generation (10/10)
RT variable name
RT Waveform length
RT.list
gen_cfg.py
Description
DB Name
FXP specifications
cfg.csv
gen_cfg.py
Ready to go
cfg.ini
&
substitutions

---
IOC compilation needed?
We now have a docker compilation environment* that compiles using a processor of another host and using the CRIO SSD
Map NFS
Map SSD using SSH
Docker on Host
Map NFS
NFS server (EPICS)
*https://gitlab.cnpem.br/SOL/Docker/dev-crio.git

---
Softwares used
- EPICS 3.15
- Synapps 6.0 (Scaler)
- Labview 2018
- 2018.5 linuxRT firmware
- Compact RIO 9035/9045

---
- Exception handling
  - Errors in the cfg.ini file, templates, or any inconsistency found appear on the EPICS IOC command prompt
    - e.g. Error on read - [LibCrioLinux] Property [RT_DBL_AI0]: Query returned null.
  - Since exceptions are redirected to epics terminal, the IOC does not stop functioning, so check your messages!

---
Known limitations
- Binary inputs are limited to 64 bits
- Moving U64, I64 (64-bits) also is lossy since these variables are converted to double in EPICS, and double is 52 bits precision

---
Nheengatu - Sharepoint
Nheengatu - git repository