CRIO-EPICS Integration
SOL

---
FPGA/Labview RT VIs
Peripherals

---
cfg.ini
EPICS IOC
NHE device support
Software
NHE library
NI FPGA lib.
LabviewRT VI
Hardware
FPGA VI
C-series module Peripherals

---
1.1 FPGA variables (1/3)
Add to your FPGA design the following patterns for all the variables (AI, AO, BI, BO) that will be exported on EPICS
Binary input : Convert to 64-bit U64
Analog input : Convert to float
Binary output : as is
Analog output : Convert to FXP

---
1.1 FPGA variables (2/3)
To implement scaler, use the following IP
Scaler digital
Scaler : IP in VHDL
Scaler Analog
Validated with testbench
If not all 64 counters are used, the logic can simply be optimized by reducing the size of the fixed input arrays.
FPGA utilization can be reduced by approximately 15% if this optimization is applied

---
1.1 FPGA variables (3/3)
Generates header file with addresses
Generate bitstream and C API files
The address of each variable must be noted for the cfg.ini file.

---
1.2 LabviewRT variables
Four Vis were developed to synchronize variable exchange with EPICs
IOC Shared memory initialize.vi
Initializes shared memory. All input can be left as default
IOC Shared memory de-initialize.vi
de-initializes shared memory.
SM read and increment.vi (polymorphic VI)
Reads the variable (from EPICS) when setting the polymorphic VI
SM write and increment.vi (polymorphic VI)
Writes the variable (to EPICS) when setting the polymorphic VI
All VI MUST be chained with <ptr in> and <ptr out>.
The index of the variable must be noted for the cfg.ini file.

---
2 & 3 libCrioLinux.so and EPICS device support
NO alteration or re-compile is required!
Device support library path needs to be indicated explicitely in the IOC

---
4.1 EPICS IOC (1/8)
As long as the associated DB files are used, the IOC does not need to be compiled either!

---
4.2 EPICS IOC – CFG.INI (2/8)
If changed, must be changed in labview RT VI too!
Disabling shared memory disables all labview RT variable processing.

---
4.2 EPICS IOC – CFG.INI (3/8)
- 2 types of variables: labview RT variables, and FPGA variables
- The library distinguishes the type and its size through its name

---
4.2 EPICS IOC – CFG.INI (4/8)
- [BIAddresses]
  - Address/index of BI
- [BI0]: index -name relation of each bit in the 64 bits (FPGA)
- [AO]: Address/index of each available output analog variable
- [AI]: Address/index of each available input analog variable
- [BO]: Address/index of each available output digital variable

---
4.2 EPICS IOC – CFG.INI (5/8)

---
4.2 EPICS IOC – Settings (6/8)
Introduce path of deviceSupportCrio to IOC
$(TOP)/configure/RELEASE
Introduce deviceSupportCrio library name to IOC
$(TOP)/CRIOApp/src/Makefile

---
4.2 EPICS IOC – st.cmd (7/8)
Once single modification : provide cfg.ini file name to crioSupSetup.

---
4.2 EPICS IOC – templates (8/8)
ai.template
This name must correspond to the name in the cfg.ini file
bi.template

---
IOC compilation needed?
We now have a docker compilation environment* that compiles using a processor of another host and using the CRIO SSD
Map NFS
Map SSD using SSH
Docker on Host
Map NFS
NFS server (EPICS)
*https://gitlab.cnpem.br/SOL/Docker/dev-crio.git

---
Softwares used
- EPICS 3.14
- Synapps 5.8 (Scaler)
- Labview 2017
- 2017 linuxRT firmware

---
Softwares used
- EPICS 3.15
- Synapps 5.8 (Scaler)
- Labview 2018
- 2018.5 linuxRT firmware

---
- Exception handling
  - Errors in the cfg.ini file, templates, or any inconsistency found appear on the EPICS IOC command prompt
    - e.g. Error on read - [LibCrioLinux] Property [RT_DBL_AI0]: Query returned null.
  - Since exceptions are redirected to epics terminal, the IOC does not stop functioning, so check your messages!
- Start beta testing

---
Known limitations
- Binary inputs are limited to 64 bits
- Analog inputs are converted to single precision (23 bits of precision). Moving data from modules that have precision of 24 bits will lossy
- Moving U64, I64 (64-bits) also is lossy since these variables are converted to double, and double is 52 bits precision
- FXP not implmented (yet)